## DX (hidden)
DX Comparison
| Ton | Mbtuh | From Study Efficiency | Calc SKW Saving (7% better) | From Study SKW | Variance | Current | Min Eff. Based on 3% better | Calc SKW Saving (3% better) | From Study SKW | Variance | Calculated | From Study SKW | SKW (@3% better EER) | Variance | EER From Study | Calculated $820/SK | 2025 | Prescriptive Program: | Processed in 2024- | Total SKW
[7 empty] | Rebate $ |  |  |  |  | Rebate $ |  |  |  |  | Rebate $ | Rebate $ | Unit Size |  |  | Minimum Efficiencies |  |  | Average | From Study | [6 empty] | Per Unit
165 | 1 | 12 | 14.5 | 0.06 |  |  | 9.9 | 13.802 | 0.023188 |  |  | 3.826 | [5 empty] | 49.2
820 | 2 | 24 | 14.5 | 0.121 |  |  | 19.965 | 13.802 | 0.046376 |  |  | 7.652 | [5 empty] | 99.22
| 2.5 | 30 | 14.5 | 0.151 |  |  | 24.915 | 13.802 | 0.05797 |  |  | 9.565 | [5 empty] | 123.82
| 3 | 36 | 14.5 | 0.181 |  |  | 29.865 | 13.802 | 0.069564 |  |  | 11.478 | [5 empty] | 148.42
| 4 | 48 | 14.5 | 0.242 |  |  | 39.93 | 13.802 | 0.092752 |  |  | 15.304 | [5 empty] | 198.44
| 5 | 60 | 14.5 | 0.302 |  |  | 49.83 | 13.802 | 0.11594 |  |  | 19.1301 | [5 empty] | 247.64 |  |  |  | SEER | SEER2 | $/ton | SkW/ton | SEER | Avg size | SkW | $/SkW | Average $ | WkW | kWh | Rebate | Tons
| 5.4 | 64.8 | 14.5 | 0.326 |  |  | 53.79 | [10 empty] | 267.32
Average |  |  |  | 0.19757 | 0.201 | -0.0034286 | 32.5993 |  | 0.067632 | 0.245 | -0.17737 | 11.1592 | 0.245 | 0.302 | 0.057 | 14.5 | 247.62 | 162.0086 | 5.4 Tons or less | 539 |  | 13.65 | 14.07 | 40.09 | 0.048896 | 14.5 | 5 | 0.24448 | 820 | 200.4736 |  |  | 220
[18 empty] | 200 | 100.9363 | 50.47% |  | 11.34 | 14.6 | 29.99 | 0.036575 | 12 | 7.5 | 0.27431 | 820 | 224.9342 |  |  | 220
[22 empty] | 10.92 | 13.97 | 20 | 0.024287 | 11.5 | 15 | 0.36431 | 823.47 | 299.9984 |  |  | 300 | 15
| 5.5 | 66 | 12 | 0.349 |  |  | 57.585 | 11.536 | 0.98763 |  |  | 162.9585 | [5 empty] | 286.18 |  |  |  | 9.77 | 12.92 | [9 empty] | 400 | 20
| 6 | 72 | 12 | 0.381 |  |  | 62.865 | 11.536 | 1.0774 |  |  | 177.7729 | [5 empty] | 312.42 |  |  |  | 9.77 | 10.5 | [9 empty] | 1200 | 60
| 6.5 | 78 | 12 | 0.413 |  |  | 68.145 | 11.536 | 1.1672 |  |  | 192.5873 | [5 empty] | 338.66 | [14 empty] | 2000 | 100
| 7 | 84 | 12 | 0.445 |  |  | 73.425 | 11.536 | 1.257 |  |  | 207.4017 | [5 empty] | 364.9
| 7.5 | 90 | 12 | 0.476 |  |  | 78.54 | 11.536 | 1.3468 |  |  | 222.2161 | 0.2743 | 0.476 | 0.2017 | 12 | 390.53 | 390.32
| 8 | 96 | 12 | 0.508 |  |  | 83.82 | 11.536 | 1.4365 |  |  | 237.0305 | [5 empty] | 416.56
| 8.5 | 102 | 12 | 0.54 |  |  | 89.1 | 11.536 | 1.5263 |  |  | 251.8449 | [5 empty] | 442.8
| 9 | 108 | 12 | 0.572 |  |  | 94.38 | 11.536 | 1.6161 |  |  | 266.6593 | [5 empty] | 469.04
| 9.5 | 114 | 12 | 0.603 |  |  | 99.495 | 11.536 | 1.7059 |  |  | 281.4737 | [5 empty] | 494.46
| 10 | 120 | 12 | 0.635 |  |  | 104.775 | 11.536 | 1.7957 |  |  | 296.2881 | [5 empty] | 520.7
| 10.5 | 126 | 12 | 0.667 |  |  | 110.055 | 11.536 | 1.8855 |  |  | 311.1025 | [5 empty] | 546.94
| 11 | 132 | 12 | 0.699 |  |  | 115.335 | 11.536 | 1.9753 |  |  | 325.9169 | [5 empty] | 573.18
| 11.25 | 135 | 12 | 0.909 |  |  | 149.985 | 11.536 | 2.0201 |  |  | 333.3241 | [5 empty] | 745.38
Average |  |  |  | 0.55362 | 0.208 | 0.34562 | 91.3465 |  | 1.5229 | 0.2743 | 1.2486 | 251.2751 | [5 empty] | 453.9646 | 5.5 Tons ≤ to 11.25 Tons | 227
[18 empty] | 400 | 85.0187 | 21.25%
| 11.5 | 138 | 11.77 | 0.73 |  |  | 120.45 | [10 empty] | 598.6
| 12 | 144 | 11.77 | 0.761 |  |  | 125.565 | [10 empty] | 624.02
| 13 | 156 | 11.77 | 0.825 |  |  | 136.125 | [10 empty] | 676.5
| 14 | 168 | 11.77 | 0.88 |  |  | 145.2 | [10 empty] | 721.6
| 15 | 180 | 11.77 | 0.952 |  |  | 157.08 |  | 0.424 | 0.36431 | 0.05969 | 347.44 | 0.36431 | 0.632 | 0.26769 | 11.5 | 518.64 | 780.64
| 16 | 192 | 11.77 | 1.015 |  |  | 167.475 | [10 empty] | 832.3
| 17 | 204 | 11.77 | 1.079 |  |  | 178.035 | [10 empty] | 884.78
| 18 | 216 | 11.77 | 1.114 |  |  | 183.81 | [10 empty] | 913.48
| 19 | 228 | 11.77 | 1.205 |  |  | 198.825 | [10 empty] | 988.1
| 19.99 | 239.88 | 11.77 | 1.268 |  |  | 209.22 |  | 621 |  |  | 102.54 |  | 0.621 |  | 10.7 | 509.58 | 1039.76
Average |  |  |  | 0.9829 | 0.2768 | 0.6752 | 162.1785 | [10 empty] | 805.978 | 11.25 Tons < to 20 Tons | 234
[18 empty] | 800 | 175.2809 | 21.91%
361.236
| 20.1 | 241.2 | 10.7 | 1.403 |  |  | 231.495 | [10 empty] | 1150.46
| 30 | 360 | 10.7 | 2.094 |  |  | 345.51 | [10 empty] | 1717.08
| 40 | 480 | 10.7 | 2.792 |  |  | 460.68 | [10 empty] | 2289.44
| 45 | 540 | 10.7 | 3.141 |  |  | 518.265 |  | 1.398 |  |  | 230.71 |  | 1.398 |  | 10.7 | 1146.55 | 2575.62
| 64 | 768 | 10.379 | 4.605 |  |  | 759.825 | [10 empty] | 3776.1
Average |  |  |  | 2.807 |  |  | 370.6531 | [10 empty] | 2301.74 | 20 Tons ≤ to 66.3 Tons | 59
[19 empty] | 0 | 5.524%
| 65 | 780 | 10.379 | 4.677 |  |  | 771.705 |  | 2.082 |  |  | 343.55 |  | 20.82 |  | 9.991 | 1707.35 | 3835.14
| 75 | 900 | 10.379 | 5.396 |  |  | 890.34 |  | 2.082 |  |  | 343.55 |  | 20.82 |  | 9.991 | 1707.35 | 4424.72
| 85 | 1020 | 10.379 | 6.116 |  |  | 1009.14 |  | 2.082 |  |  | 343.55 |  | 20.82 |  | 9.991 | 1707.35 | 5015.12
Average |  |  |  | 5.3963 |  |  | 890.395 | [10 empty] | 4424.9933 | ≥ 63.3 Tons | 9
|  |  | SkW | 48.567 | [14 empty] | 0 | 0.8427%
[19 empty] | Total Unit processed | 1068
|  |  | Total SkW | 48.567 | [14 empty] | Total SkW processed | 1550.439

## VFD Calcs
[7 empty] | Existing | Proposed
[5 empty] | Annual Hours of Operation: |  | 3120 | 3120
Output | Percent | Existing | Proposed | kW | Estimated | Existing | Proposed | Energy |  | Assumptions:
Load | of full | w/o VFD | w/VFD | Demand | %Time at | w/o VFD | w/VFD | Savings |  | 1. Output load level = max system peak/On-peak Hr Max peak load; since FPL summer peaking hours is from June to September from 3-6PM, max system capacity during the on-peak hours vs overall system max capacity
Level | load speed | kW | kW | Saving | Load | kWh | kWh | kWh |  | 2. Output Load Level=Percent Speed
40% | 40% |  |  |  | 0% | 0 | 0 | 0
45% | 45% | 37.3 | 9.3153 | 27.9847 | 0% | 0 | 0 | 0
50% | 50% | 37.3 | 11.2014 | 26.0986 | 0% | 0 | 0 | 0
55% | 55% | 37.3 | 13.2345 | 24.0655 | 0% | 0 | 0 | 0
60% | 60% | 37.3 | 15.4113 | 21.8887 | 5% | 5818.8 | 2404.1575 | 3414.6425
65% | 65% | 37.3 | 17.7285 | 19.5715 | 5% | 5818.8 | 2765.6461 | 3053.1539
70% | 70% | 37.3 | 20.1834 | 17.1166 | 15% | 17456.4 | 9445.8503 | 8010.5497
75% | 75% | 37.3 | 22.7736 | 14.5264 | 15% | 17456.4 | 10658.0242 | 6798.3758
80% | 80% | 37.3 | 25.4965 | 11.8035 | 15% | 17456.4 | 11932.377 | 5524.023
85% | 85% | 37.3 | 28.3502 | 8.9498 | 20% | 23275.2 | 17690.5505 | 5584.6495
90% | 90% | 37.3 | 31.3327 | 5.9673 | 15% | 17456.4 | 14663.7106 | 2792.6894
95% | 95% | 37.3 | 34.4421 | 2.8579 | 5% | 5818.8 | 5372.9716 | 445.8284
100% | 100% | 37.3 | 37.6768 | -0.37677 | 5% | 5818.8 | 5877.5758 | -58.7758
|  |  | TOTALS |  | 100% | 116376 | 80810.8637 | 35565.1363
System Type | Condenser Water Pump
Pump Motor Horse Power (HP) | 50
Quantity | 1 | [9 empty] | Based ASHRAE Standard Run Time Average
Max Peak Load (tons) | 390 | Max System Peak Load | [9 empty] | % run time | Weighted Average
On-Peak Hr Max Peak Load (tons) | 351 | Summer month 3-6 PM Peak Load | [9 empty] | 2% | 0%
Motor Efficiency Value | 90% | [10 empty] | 43% | 0%
Average VFD Efficiency Penalty | 1% | [10 empty] | 40% | 0%
Existing w/o VFD kW | 37.3 | [10 empty] | 13% | 0%
Proposed w/VFD kW | 31.3327 | [11 empty] | 0%
kWh Factor | 8930.52
WKW Factor | 4.618 | [9 empty] | VFD installed cost average: $/HP |  |  | 500
System Estimated Peak Load % | 90% | [9 empty] | Total Installed Average Cost |  |  | 25000
Motor kW at System Peak Load (kW) | 37.3
Total Motor kW at System Peak Load (kW) | 37.3 | [12 empty] | 38.19%
Rebate Amount $/kW | 1600
Total Summer kWD Reduction | 5.9673
Total Winter kWD Reduction | 27.5569 | [9 empty] | Held pump wheel diameter constant: (D1/D2)^3=1 |  | exponent
Total kWh Reduction | 53290.9578 | [9 empty] | P1=P2 x ((n1/n2)^exp) |  | 3
Rebate Amount | 9547.656 | [9 empty] | q1=q2 x (n1/n2)
[11 empty] | Percent Input Power | Percent Speed | p1 | p2 | q1 | q2 | n1 | n2 | n1/n2
VFD Parameters | [10 empty] | 100% | 100% | 10 | 10 | 1000 | 1000 | 3500 | 3500 | 1
Power-to-Speed Reduction Exponent | 1.75 | [9 empty] | 99.52% | 98.57% | 9.9522 | 10 | 985.7143 | 1000 | 3450 | 3500 | 0.98571
Power-to-Speed Reduction Exponent Chiller | 2.5 | Chilled Water Pump | [8 empty] | 98.55% | 95.71% | 9.8551 | 10 | 957.1429 | 1000 | 3350 | 3500 | 0.95714
Power-to-Speed Reduction Exponent Condenser | 1.75 | Condenser Water Pump | [8 empty] | 97.56% | 92.86% | 9.756 | 10 | 928.5714 | 1000 | 3250 | 3500 | 0.92857
IDENTIFY EXISTING METHOD OF CONTROL | 1 | [9 empty] | 96.55% | 90% | 9.6549 | 10 | 900 | 1000 | 3150 | 3500 | 0.9
1=No Control, 2=Pump Throttling | 1 or 2 | [9 empty] | 95.52% | 87.14% | 9.5516 | 10 | 871.4286 | 1000 | 3050 | 3500 | 0.87143
HP-KW factor | 0.746 | [9 empty] | 94.46% | 84.29% | 9.4461 | 10 | 842.8571 | 1000 | 2950 | 3500 | 0.84286
Curve Equations | [10 empty] | 93.38% | 81.43% | 9.3381 | 10 | 814.2857 | 1000 | 2850 | 3500 | 0.81429
[11 empty] | 92.28% | 78.57% | 9.2276 | 10 | 785.7143 | 1000 | 2750 | 3500 | 0.78571
% Power = a x % speed^2 + b x % speed + c | [10 empty] | 91.14% | 75.71% | 9.1144 | 10 | 757.1429 | 1000 | 2650 | 3500 | 0.75714
[11 empty] | 89.98% | 72.86% | 8.9982 | 10 | 728.5714 | 1000 | 2550 | 3500 | 0.72857
Coefficients | [5 empty] | a |  | b | c |  | 88.79% | 70% | 8.879 | 10 | 700 | 1000 | 2450 | 3500 | 0.7
[11 empty] | 87.57% | 67.14% | 8.7566 | 10 | 671.4286 | 1000 | 2350 | 3500 | 0.67143
pump throttling or fan/blower discharge damper | [5 empty] | -0.4375 |  | 1.0261 | 0.4107 |  | 86.31% | 64.29% | 8.6305 | 10 | 642.8571 | 1000 | 2250 | 3500 | 0.64286
[11 empty] | 85.01% | 61.43% | 8.5007 | 10 | 614.2857 | 1000 | 2150 | 3500 | 0.61429
[11 empty] | 83.67% | 58.57% | 8.3668 | 10 | 585.7143 | 1000 | 2050 | 3500 | 0.58571
Pump Motor Power Requirements | [10 empty] | 82.29% | 55.71% | 8.2285 | 10 | 557.1429 | 1000 | 1950 | 3500 | 0.55714
[11 empty] | 80.85% | 52.86% | 8.0854 | 10 | 528.5714 | 1000 | 1850 | 3500 | 0.52857
Percent Full | Percent of Full Speed Input Power with | [9 empty] | 79.37% | 50% | 7.937 | 10 | 500 | 1000 | 1750 | 3500 | 0.5
Speed |  | Discharge | Ideal
Flow | No control | Throttling | VFD
100% | 100% | 100% | 100%
80% | 100% | 95% | 51.2%
60% | 100% | 87% | 21.6%
40% | 100% | 75% | 6.4%
20% | 100% | 60% | 0.8%
0% | 100% | 41% | 0%
Notes | 1 | 2 | 3
System equation:
"- a(System Estimated Peak Load %)*2 + b(System Estimated Peak Load %) + c"
a=-0.4375
b=1.0261
c=0.417
References: https://www.efficiencymaine.com/docs/VFD-Savings-Analysis.xls
Generic VFD Savings Calculation Spreadsheet
The user should input project specific data into the yellow shaded cells.
C28 describe the motor(s) being controlled in terms of HP, % loading at 100% output level for the process, and motor nominal efficiency.
Power-to-Speed Reduction Exponent: When friction represents a high % of overall head, the exponent is closer to 3.0 and the input power with vfd will follow affinity laws (input power varies as the cube of % speed). Open systems where head loss is not mainly from friction losses, the exponent should be closer between 1-2
Cell E37, E38 and E39 should be populated with VFD manufacturers data.
Cell F33 represent the method of control that most closer describes the baseline situation.
Cells H43 and I43 represent the annual hours of operation for the baseline and the proposed case.
The range from cell B47:D59 should be used to describe the load shape of the operation. Inputs to this range should be supported by historical data, or clearly explained.
Note on S23: Lui, Chi: Get actual data from Richard Brooks
Note on C30: Lui, Chi: 8930.5: Resource Innovation data
Note on B31: Lui, Chi: Include winter kw factor
Note on B32: Lui, Chi: Assume system estimated peak load = system estimated VFD speed
Note on C37: Lui, Chi: WKW calculation

## Vlocity Matrices (hidden)
DSM specialist inputs
System Type: | Drop Down selection: Chilled water pump, Condenser water pump (select one) | Period (Text) | Program (Text) | Measure (Text) | Average VFD penalty (%): | kWh Factor: | Winter kW Factor: | HP-KW factor | Rebate amount ($/kW): | Power-to-Speed Reduction Exponent Chiller | Power-to-Speed Reduction Exponent Condenser | a: coefficient-a | b: coefficient-b | c: coefficient-c
Number of Units: | input number value | Current | Business HVAC - VFD | Variable Frequency Drive | 0% | 8930.52 | 4.618 | 0.746 | 1600 | 2.5 | 1.75 | -0.4375 | 1.0261 | 0.4107
Pump Motor Horse Power (HP): | input number value | Grace | Business HVAC - VFD | Variable Frequency Drive | 0% | 8930.52 | 4.618 | 0.746 | 1600 | 2.5 | 1.75 | -0.4375 | 1.0261 | 0.4107
Max Peak load (tons): | input number value
On-peak Max Load (tons): | input number value
Motor Efficiency Value (%): | Input Percent value
Existing System Control Method (number value) | Drop Down selection: No control, Pump Throttling (select one)
Program manager inputs
Average VFD penalty (%): | 0%
kWh Factor: | 8930.52
Winter kW Factor: | 4.618
HP-KW factor | 0.746
Rebate amount ($/kW): | 1600
Power-to-Speed Reduction Exponent Chiller | 2.5
Power-to-Speed Reduction Exponent Condenser | 1.75
a: coefficient-a | -0.4375
b: coefficient-b | 1.0261
c: coefficient-c | 0.4107
Back end Calculations | Refer to VFD Calcs
System Estimated Peak Load (%) = | On-Peak Hr Max Peak Load / Max Peak Load
Motor kW at System Peak Load (kW) = | HP-kW factor * Pump Motor Horse Power * System Estimated Peak Load / Motor Efficiency Value
Control Method-1: Existing w/o VFD kW = | Motor kW at System Peak Load
Control Method-2: Existing w/o VFD kW = | coefficient-a * System Estimated Peak Load^2 + coefficient -b * System Estimated Peak Loa + coefficient-c
Proposed w/VFD kW (Chilled Water Pump) = | System Estimated Peak Load^Power-to-Speed Reduction Exponent Chiller * Motor kW at System Peak Load / (1-Average VFD penalty)
Proposed w/VFD kW (Condenser Water Pump) = | System Estimated Peak Load^Power-to-Speed Reduction Exponent Condenser * Motor kW at System Peak Load / (1-Average VFD penalty)
Total Motor kW at System Peak Load (Chilled Water Pump) = | Proposed w/VFD * Number of Units
Total Motor kW at System Peak Load (Condenser Water Pumpp) = | Proposed w/VFD * Number of Units
Total Summer kWD Reduction = | Existing w/o VFD kW (Use selected Method 1 or Method 2) - Total Motor kW at System Peak Load (Use selected Chilled Water Pump or Condenser Water Pump)
Total Winter kWD Reduction= | Total Summer kWD Reduction*Winter kW Factor
Total kWh Reduction = | Total Summer kWD Reduction*kWh Factor
Rebate Amount = | Total Summer kWD Reduction * Rebate Amount
Outputs
Pump Motor Horse Power = | From input value
Number of units = | From input value
Total Summer kWD Reduction = | From backend calculations
Total Winter kWD Reduction= | From backend calculations
Total kWh Reduction = | From backend calculations
Rebate Amount = | From backend calculations

## Required Documents (hidden)
Required Documents
Schedule of values/Invoice/Purchase order
Peak Day Load Profile
Variable Frequency Drive Submittals
Pump Submittals
Pump schedules/Mechanical schedules

## Sheet1 (hidden)
| AC | AC | WC | AC | AC | AC | Average
tonnage | 120 | 250 | 800 | 200 | 140 | 300 | 301.6667
skw | 10 | 40 | 25 | 20 | 15 | 30 | 23.3333
Water flow | [6 empty] | 724
VFD (skw) | [6 empty] | 5 | 0.21429
720