## DXAC Prog and Lookup
Program Manager Inputs - Part of Vlocity Matrices
Program Specialist Inputs/Selections
Backend Calculation Formulas
DX Program Level Inputs
|  | Qualifier factor - x% better than MinQual | 107% | Qualifier | Base | Qualifier | Base | Qualifier | Base | Qualifier | Base | Qualifier
|  |  | (S)EER2 Base | (S)EER2 | SEER | SEER | EER | EER | IEER2 | IEER2 | IEER | IEER
|  | Minimum Qualified Efficiency for less than 65 Mbtuh | 13.814 | 14.781 | 14.4624 | 15.4748
|  |  | 12.0963 | 12.9431 | 12.0963 | 12.9431 | [6 empty] | Min_EER_65 |  | Fundamental base equation:
|  | Minimum Qualified Efficiency for 65 ≤ MBtuh < 135 |  |  |  |  | 11.202 | 11.9861 | 14.8 | 15.836 | 14.8 | 15.836 | Min_EER_65_135 |  | kWat the meter = | (Unit Capacity Mbtuh/12 * (12/EERbase – 12/EERnew)) * BES Factor
|  | Minimum Qualified Efficiency for 135 ≤ MBtuh < 240 |  |  |  |  | 11.002 | 11.7721 | 14.2 | 15.194 | 14.2 | 15.194 | Min_EER_135_240 |  | Unit Capacity Mbtuh/12: | Conversion Mbtuh to Ton
|  | Minimum Qualified Efficiency for 240 ≤ MBtuh < 760 |  |  |  |  | 10.002 | 10.7021 | 13.2 | 14.124 | 13.2 | 14.124 | Min_EER_240_760 |  | 12/EERbase: | Conversion EE_SEER2_IEER to KW/Ton
|  | Minimum Qualified Efficiency for MBtuh ≥ 760 |  |  |  |  | 9.702 | 10.3811 | 12.5 | 13.375 | 12.5 | 13.375 | MIN_EER_760 |  | 12/EERnew: | Conversion EE_SEER2_IEER to KW/Ton
|  | Capacity 65 Mbtuh | 65 | [9 empty] | Capacity_65_Mbtuh
|  | Capacity 135 Mbtuh | 135 | [9 empty] | Capacity_135_Mbtuh |  | Qualification criteria calculations applied prior to calculation of Indicators
|  | Capacity 240 Mbtuh | 240 | [9 empty] | Capacity_240_Mbtuh
|  | Capacity 760 Mbtuh | 760 | [9 empty] | Capacity_760_Mbtuh |  | Transformation equations to SkW, WkW, GWh, Incentive (OUTPUT):
|  | FPL Rebate $/KW ===> | 820 | [9 empty] | FPL_Rebate |  | Indicator = | Factor per kW * kWon premise
|  | Capacity Range less than 5.4 tons | 200 | [9 empty] | BES_Factor |  | Indicator (Summer KW Reduction) = | Summer KW Factor * Summer KW Reduction
|  | Capacity Range greater than 5.4 tons, less than 11.25 tons | 400 | [9 empty] | SEER2_Factor_less_than_65_Mbtuh |  | Indicator (Winter KW Reduction) = | Winter KW Factor * Summer KW Reduction
|  | Capacity Range greater than 11.25 tons, less than 20 tons | 800
|  | BES Factor | 0.889
|  | Factor Less Than 65 Mbtuh and Heat Pump | 1.142
|  | SEER2 Factor less than 65 Mbuth | 1.0469
|  | EER Factor greater than 65 Mbtuh | 1.0428 | [9 empty] | Base_IEER_to_EER_Factor_more_than_65_Mbtuh
|  | IEER Factor greater than 65 Mbtuh | 1 | [9 empty] | New_IEER_to_EER_Factor_more_than_65_Mbtuh |  | Indicator (KWh Reduction) = | KWh Factor * Summer KW Reduction
|  | Summer kW Factor | 1 | [9 empty] | Summer_kW_Factor
|  | Winter kW Factor | 0.5493 | [9 empty] | Winter_kW_Factor |  | Rebate Amount:
|  | kWh Factor | 6201.51 | [9 empty] | kWh_Factor |  | Rebate Amount = | Summer KW Reduction * FPL Rebate
|  | Water Cooled Weighted Average | 0.851 | [9 empty] | Heat_Pump
|  | Heat Pump | Yes | [11 empty] | Data Validation:
No
|  | EFFICIENCY CONDITIONS | [11 empty] | 29 | EER | System Capacity must be >= 65Mbtuh
|  | Base Efficiency EER Qualifier | 0 | [10 empty] | 30 | SEER2 | System Capacity must be < 65Mbtuh
|  | Base Efficiency SEER Qualifier | 0 | [10 empty] | 31 | IEER
|  | Base Efficiency SEER2 Qualifier | 0 | [10 empty] | 32 | SEER
| new field | Base Efficiency IEER Qualifier | 0 | [10 empty] | 33 | EER2
|  | Base Efficiency EER2 Qualifier | 12.9431 | [10 empty] | 34 | IEER2
|  | Base Efficiency IEER2 Qualifier | 0
|  | Calculated Base Efficiency | 12.0963 | [9 empty] | Calculated_Base_Efficiency |  | SEER Factor less than 65 Mbuth | 1.0469 | Convert SEER2 to SEER value
|  | Calculated New Efficiency | 17 | [9 empty] | Calculated_New_Efficiency |  | EER Factor greater than 65 Mbtuh | 1.0426 | Convert EER to EER2 value
|  | Qualification | Qualify | [11 empty] | IEER_EER2 Factor greater than 65 Mbtuh | 1.246
[15 empty] | IEER_IEER2 Factor greater than 65 Mbtuh | 1 | Convert IEER to IEER2 value
Direct Expansion Unit (DX)
|  | Efficiency Rating | EER2
|  | Heat Pump | Yes | [11 empty] | DNQ | Do Not Qualify
|  | Water Cooled | Yes | [11 empty] | Qualify
|  | System Capacity (Mbtuh) | 64
|  | New Equipment Efficiency | 17 | [11 empty] | System Capacity | Minimum Efficiency | Rebate Amount
|  | Quantity | 1 | [11 empty] | Less than 65 MBTUH | SEER2: 14.78 | $200 per unit
[15 empty] | Equal to 65 MBTUH and less than 135 MBTUH | EER: 11.98 | $400 per unit
|  | Results | [12 empty] | Equal to 135 MBTUH and less than 240 MBTUH | EER: 11.77 | $800 per unit
|  |  | POST 2025 | PRE 2025 | [10 empty] | Equal to 240 MBTUH and less than 760 MBTUH | EER: 10.70 | $820 per summer kW reduction
|  | KW Reduction at Meter | 1.1546 | 1.1546 | [10 empty] | Equal to 760 MBTUH and greater | EER: 10.38 | $820 per summer kW reduction
|  | Summer KW Reduction (SKW) | 1.1546 | 1.1546
|  | Winter KW Reduction (WKW) | 0.63422 | 0.63422 |  | Do not delete | [9 empty] | 2025 Expansion factor | At Generator
|  | kWh Reduction (KWH) | 7160.2535 | 7160.2535 |  | 1.1546 | 0 | 0.98256 | [6 empty] | SKW | 1.0745 | 1.2406
| revised formula | Incentive | 200 | 190.5087 |  |  | 0.98256 | 0.98256 | [6 empty] | KWH | 1.0579 | 7574.8322
|  | For additional support: | [5 empty] | 0.53972
|  | Business HVAC Program Support: | Mike.Catarzi@fpl.com |  |  |  |  | 6093.3757
|  | Business HVAC Program Support: | Jared.Giordano@fpl.com |  |  | 165 |  | 200 | [6 empty] | SkW Factor
|  | Busines HVAC Technical Support: | Chi.Lui@fpl.com | [11 empty] | Winter kW factor
|  | Busines HVAC Technical Support: | Abel.Alonso@fpl.com | [11 empty] | KWH Factor
|  | BES | Code
|  | Factor | 7%
|  | 88.9% | EER =>
EER to SEER
| Rebate | 2 | 3 | [9 empty] | >=760 Mbtuh |  |  | 240 =< Mbtuh < 760 MBtuh |  |  | 135 =< Mbtuh < 240 MBtuh |  |  | 65 =< Mbtuh < 135 Mbtuh |  |  | < 65 MBtuh |  | 82%
| Paym $/kw | [11 empty] | EER Basis |  | Qualify | EER Basis |  | Qualify | EER Basis |  | Qualify | EER Basis |  | Qualify | SEER Basis |  | Qualify
| 165 | [11 empty] | 9.7 |  | 9.979 | 10 |  | 10.5 | 11 |  | 11.47 | 11.2 |  | 11.984 | 13.4 |  | 14.038
FPL Rebates DX
Must Meet Efficiency Standards ASHRAE 90.1
| 1 | Eff | Eff | [9 empty] | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
| Dx Unitary | KW/TON | COP
| Cap Tons | 1.2 | 2.9308 | [9 empty] | 4: Tons ≥ 63.33; 7: 20 ≤ Tons < 63.33; 10: 11.25 ≤ Tons < 20; 13: 5.42 ≤ Tons < 11.25; 16: Tons < 5.42
| Cap MBtuh | 1.143 | 3.0774 | [9 empty] | 4: MBtuh ≥ 760; 7: 240 ≤ MBtuh < 760; 10: 135 ≤ MBtuh < 240; 13: 65 ≤ MBtuh < 135; 16: MBtuh < 65
|  | 1.091 | 3.2239
| Eff | 1.043 | 3.3705 | [9 empty] | Rebate >63 |  | Reduction | Rebate 20 to 63 |  | Reduction | Rebate |  | Reduction | Rebate |  | Reduction | Rebate |  | Reduction
| (S)EER | 1 | 3.517 | [9 empty] | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh | $/MBtuh | $/tons | kW/MBtuh
| 10 | 0.96 | 3.6635 | [9 empty] | 4: 0.61875; 5: 7.425; 6: 0.0028
| 10.5 | 0.923 | 3.8101 | [9 empty] | 4: 1.3117; 5: 15.741; 6: 0.007; 7: 0.8415; 8: 10.098; 9: 0.0042
| 11 | 0.889 | 3.9566 | [9 empty] | 4: 1.5202; 5: 18.2427; 6: 0.0108; 7: 1.485; 8: 17.82; 9: 0.0081
| 11.5 | 0.857 | 4.1032 | [9 empty] | 1.6414 | 19.6965 | 0.0144 | 1.6027 | 19.2327 | 0.0116 | 0.71775 | 8.613 | 0.0036
| 12 | 0.828 | 4.2497 | [9 empty] | 1.8171 | 21.805 | 0.0176 | 1.76 | 21.12 | 0.0148 | 1.2293 | 14.751 | 0.0067 | 0.693 | 8.316 | 0.0053
| 12.5 | 0.8 | 4.3962 | [9 empty] | 2.0175 | 24.2105 | 0.0205 | 1.8162 | 21.795 | 0.0178 | 1.3817 | 16.5805 | 0.0097 | 0.8712 | 10.4544 | 0.0083
| 13 | 0.774 | 4.5428 | [9 empty] | 2.1879 | 26.2548 | 0.0233 | 1.8777 | 22.5324 | 0.0205 | 1.4784 | 17.7412 | 0.0124 | 1.3167 | 15.8004 | 0.011
| 13.5 | 0.75 | 7 | [9 empty] | 2.6004 | 31.2048 | 0.0258 | 2.2968 | 27.5616 | 0.023 | 1.6962 | 20.3544 | 0.015 | 1.7358 | 20.8296 | 0.0135 | 1.254 | 15.048 | 0.0006
| 14 | 0.727 | 4.8359 | [9 empty] | 2.9964 | 35.9568 | 0.0282 | 2.6862 | 32.2344 | 0.0254 | 2.0823 | 24.9876 | 0.0173 | 2.1252 | 25.5024 | 0.0159 | 1.65 | 19.8 | 0.0035
| 14.5 | 0.706 | 4.9824 | [9 empty] | 3.3429 | 40.1148 | 0.0303 | 3.0459 | 36.5508 | 0.0276 | 2.4387 | 29.2644 | 0.0195 | 2.4783 | 29.7396 | 0.018 | 1.9965 | 23.958 | 0.0061
| 15 | 0.686 | 5.129 | [9 empty] | 3.6894 | 44.2728 | 0.0324 | 3.3825 | 40.59 | 0.0296 | 2.7852 | 33.4224 | 0.0216 | 2.8215 | 33.858 | 0.0201 | 2.343 | 28.116 | 0.0086
| 15.5 | 0.667 | 5.2755 | [9 empty] | 4.0029 | 48.0348 | 0.0343 | 3.7059 | 44.4708 | 0.0316 | 3.0987 | 37.1844 | 0.0235 | 3.1383 | 37.6596 | 0.022 | 2.6565 | 31.878 | 0.011
| 16 | 0.649 | 5.422 | [9 empty] | 4.2999 | 51.5988 | 0.0361 | 3.993 | 47.916 | 0.0333 | 3.3957 | 40.7484 | 0.0253 | 3.432 | 41.184 | 0.0238 | 2.9535 | 35.442 | 0.0132
| 16.5 | 0.632 | 5.5686 | [9 empty] | 4.5804 | 54.9648 | 0.0378 | 4.2768 | 51.3216 | 0.035 | 3.6762 | 44.1144 | 0.027 | 3.7158 | 44.5896 | 0.0255 | 3.234 | 38.808 | 0.0152
| 17 | 0.615 | 5.7151 | [9 empty] | 4.8444 | 58.1328 | 0.0394 | 4.5342 | 54.4104 | 0.0366 | 3.9303 | 47.1636 | 0.0285 | 3.9732 | 47.6784 | 0.0271 | 3.498 | 41.976 | 0.0171
| 17.5 | 0.6 | 5.8617 | [9 empty] | 5.0886 | 61.0632 | 0.0408 | 4.7817 | 57.3804 | 0.0381 | 4.1778 | 50.1336 | 0.03 | 4.2207 | 50.6484 | 0.0286 | 3.7455 | 44.946 | 0.0189
| 18 | [11 empty] | 5.3196 | 63.8352 | 0.0422 | 5.0127 | 60.1524 | 0.0395 | 4.4088 | 52.9056 | 0.0314 | 4.4517 | 53.4204 | 0.03 | 3.9765 | 47.718 | 0.0207
| 18.5 | [11 empty] | 5.5374 | 66.4488 | 0.0436 | 5.2272 | 62.7264 | 0.0408 | 4.6233 | 55.4796 | 0.0327 | 4.6662 | 55.9944 | 0.0313 | 4.191 | 50.292 | 0.0223
| 19 | [11 empty] | 5.7486 | 68.9832 | 0.0448 | 5.4417 | 65.3004 | 0.0421 | 4.8378 | 58.0536 | 0.034 | 4.8807 | 58.5684 | 0.0326 | 4.4055 | 52.866 | 0.0238
| 19.5 | [11 empty] | 5.9499 | 71.3988 | 0.0461 | 5.643 | 67.716 | 0.0433 | 5.0457 | 60.5484 | 0.0353 | 5.082 | 60.984 | 0.0338 | 4.6035 | 55.242 | 0.0253
| 20 | [11 empty] | 6.1314 | 73.5768 | 0.0472 | 5.8335 | 70.002 | 0.0445 | 5.2272 | 62.7264 | 0.0364 | 5.2668 | 63.2016 | 0.0349 | 4.785 | 57.42 | 0.0267
|  | DX Qualify | #NAME?
|  | kW @ Meter | #NAME? | [9 empty] | 4: MBtuh ≥ 760; 7: 240 ≤ MBtuh < 760; 10: 135 ≤ MBtuh < 240; 13: 65 ≤ MBtuh < 135; 16: MBtuh < 65
kW Lookup | [12 empty] | 4: #NAME?; 7: #NAME?; 10: #NAME?; 13: #NAME?; 16: #NAME?
Incentive Lookup | [12 empty] | 4: #NAME?; 7: #NAME?; 10: #NAME?; 13: #NAME?; 16: #NAME?
Note on D6: Lui, Chi: Added factor, new effiiency must be better by 7%
Note on J10: Lui, Chi: Added IEER Baseline
Note on D24: Lui, Chi: New Factor
Note on D25: Lui, Chi: New Factor =1/0.959
Note on D26: Lui, Chi: Changed name From New IEER to EER Factor more than 65 Mbtuh
Note on D35: Lui, Chi: Added EER2 and IEER2 options
Note on D36: Deleted SEER_Factor less than 65 Mbtuh from equation. Added EER2 and IEER2 options
Note on D37: Lui, Chi: Deleted SEER_Factor less than 65 Mbtuh from equation. Added EER2 and IEER2 options
Note on D38: Lui, Chi: Mult;iply by new IEER_IEER2 Factor greater than 65 Mbtuh
Note on C41: Lui, Chi: Changed name from
Note on D41: Lui, Chi: cahnged equiation
Note on C50: Lui, Chi: changed name from New EER/SEER/SEER2/IEER to New Equipment Efficiency
Note on AB73: LSN0HTR: SEER to EER Factor provided by AHRI DATA BASE
Note on P75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.4 to accomodate the 10.0 value in the table
Note on S75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced by 0.3 to accomodate the 10.5 value in the table
Note on V75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.3 to accomodate the 11.5 value in the table
Note on AB75: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Baseline reduced 0.3 to accomodate the 14.0 value in the table
Note on AB105: LSN0HTR: kW /ton Reduction =[(12/Base SEER*.82) -(New (kW/Ton)/.82))*BES Impact Factor]*1 ton/12MBtuh

## ASHRAE Std 90.1 (hidden)
Table 6.8.1-1 Electrically Operated Unitary Air Conditioners and Condensing Units - Minimum Efficiency Requirements
Air Conditioners, Air-Cooled
Water Cooled
Size Category | Heating Type | SEER | SEER2 | EER | IEER | Factor |  |  |  | EER
< 65 Mbtuh | All | 13 | 13.4 |  |  | 1.1074 | (given) |  |  | 12.1 | 1.0744
≥ 65 Mbtuh and < 135 Mbtuh | Electric Resistence or none |  |  | 11.2 | 14.8 | 1.3214 |  |  |  | 12.1 | 0.92562
≥ 65 Mbtuh and < 135 Mbtuh | All Other |  |  | 11 | 14.6 | 1.3273 |  |  |  | 11.9 | 0.92437
≥ 135 Mbtuh and < 240 Mbtuh | Electric Resistence or none |  |  | 11 | 14.2 | 1.2909 |  |  |  | 12.5 | 0.88
≥ 135 Mbtuh and < 240 Mbtuh | All Other |  |  | 10.8 | 14 | 1.2963 |  | 1.3082 |  | 12.3 | 0.87805
≥ 240 Mbtuh and < 760 Mbtuh | Electric Resistence or none |  |  | 10 | 13.2 | 1.32 |  |  |  | 12.4 | 0.80645
≥ 240 Mbtuh and < 760 Mbtuh | All Other |  |  | 9.8 | 13 | 1.3265 |  |  |  | 12.2 | 0.80328
≥ 760 Mbtuh | Electric Resistence or none |  |  | 9.7 | 12.5 | 1.2887 |  |  |  | 12.2 | 0.79508
≥ 760 Mbtuh | All Other |  |  | 9.5 | 12.3 | 1.2947 |  |  |  | 12 | 0.79167
0.85056
`
Table 6.8.1-2 Electrically Operated Unitary Heat Pumps - Minimum Efficiency Requirements | [8 empty] | 1.3038
Air-Cooled (cooling mode)
Size Category | Heating Type | SEER | SEER2 | EER | IEER | Factor
< 65 Mbtuh | All | 14 | 14.3 |  |  | 1.0214 | (given)
≥ 65 Mbtuh and < 135 Mbtuh | Electric Resistence or none |  |  | 11 | 14.1 | 1.2818
≥ 65 Mbtuh and < 135 Mbtuh | All Other |  |  | 10.8 | 13.9 | 1.287
≥ 135 Mbtuh and < 240 Mbtuh | Electric Resistence or none |  |  | 10.3 | 13.5 | 1.3107
≥ 135 Mbtuh and < 240 Mbtuh | All Other |  |  | 10.4 | 13.3 | 1.2788 |  | 1.2995
≥ 240 Mbtuh and < 760 Mbtuh | Electric Resistence or none |  |  | 9.5 | 12.5 | 1.3158
≥ 240 Mbtuh and < 760 Mbtuh | All Other |  |  | 9.3 | 12.3 | 1.3226
10
Table 6.8.1-2 Electrically Operated Unitary Heat Pumps - Minimum Efficiency Requirements
Size Category | Heating Type | EER Water Cooled | SEER2 Air Cooled
Water Cooled
< 65 Mbtuh only | All | 12.1 | 13.814
Factor-water-Air |  | 1.1417
SEER | SEER2 | SEER_SEER2
12 | 11.5 | 1.0435
13 | 12.4 | 1.0484
14 | 13.4 | 1.0448
15 | 14.3 | 1.049
16 | 15.3 | 1.0458
17 | 16.2 | 1.0494
18 | 17.2 | 1.0465
19 | 18.1 | 1.0497
20 | 19.1 | 1.0471
21 | 20.1 | 1.0448
22 | 21 | 1.0476
23 | 22 | 1.0455
24 | 22.9 | 1.048
25 | 23.9 | 1.046
26 | 24.8 | 1.0484
27 | 25.8 | 1.0465
28 | 26.7 | 1.0487
29 | 27.7 | 1.0469
30 | 28.7 | 1.0453
|  | 1.0469 | 0.95517
EER | EER2
6 | 5.8 | 1.0345
7 | 6.7 | 1.0448
8 | 7.7 | 1.039
9 | 8.6 | 1.0465
10 | 9.6 | 1.0417
11 | 10.5 | 1.0476
12 | 11.5 | 1.0435
13 | 12.5 | 1.04
14 | 13.4 | 1.0448
15 | 14.4 | 1.0417
16 | 15.3 | 1.0458
17 | 16.3 | 1.0429
18 | 17.3 | 1.0405
19 | 18.2 | 1.044
20 | 19.2 | 1.0417
|  | 1.0426 | 0.95916
https://nee.sharepoint.com/:x:/r/teams/EXT_EXTDSMSProjectTeamsChannel/_layouts/15/Doc.aspx?sourcedoc=%7BA7941B36-3EC4-4E18-B673-C26F641D505C%7D&file=Business%20HVAC%20DX%20Calculation%20R4-07312023.xlsx&action=default&mobileredirect=true

## Vlocity Matrices (hidden)
[6 empty] | Back End | Back End |  | Back end
Input Data |  |  |  | Output Data
Period (Text) | Program (Text) | Measure (Text) | System Capacity Mbtuh (Range) | Qualifier Factor (%) | Min Qual Efficiency SEER2 (#) | Min Qual Efficiency SEER (#) | Min Qual Efficiency EER2 (#) | Min Qual Efficiency EER (#) | Min Qual Efficiency IEER2 (#) | Min Qual Efficiency IEER (#) | SEER2AppBelowMbtuh (#) | SEER Factor (#) | Heat Pump Factor (#) | EERIEERAppAboveMbtuh (#) | EER Factor (#) | IEER Factor (#) | BESFactor (#) | Water Cooled Weighted Avg (#) | Summer kW Factor (#) | WinterkWFactor (#) | kWh Factor (#) | Rebate Amount (#)
Current | Business HVAC - DXAC | Direct Expansion AC | 64.99 | 107% | 13.814 | 14.4633 | 12.0963 | 99999 | 99999 | 99999 | 65 | 1.047 | 1.142 | 99999 | 99999 | 99999 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 200
Current | Business HVAC - DXAC | Direct Expansion AC | 65 | 107% | 99999 | 99999 | 10.7402 | 11.202 | 14.8 | 14.8 | 65 | 99999 | 99999 | 65 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 400
Current | Business HVAC - DXAC | Direct Expansion AC | 135 | 107% | 99999 | 99999 | 10.5484 | 11.002 | 14.2 | 14.2 | 65 | 99999 | 99999 | 135 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 800
Current | Business HVAC - DXAC | Direct Expansion AC | 240 | 107% | 99999 | 99999 | 9.5896 | 10.002 | 13.2 | 13.2 | 65 | 99999 | 99999 | 240 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 820
Current | Business HVAC - DXAC | Direct Expansion AC | 760 | 107% | 99999 | 99999 | 9.302 | 9.702 | 12.5 | 12.5 | 65 | 99999 | 99999 | 760 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 820
Current | Business HVAC - DXAC | Direct Expansion HP | 64.99 | 107% | 13.814 | 14.4633 | 12.0963 | 99999 | 99999 | 99999 | 65 | 1.047 | 1.142 | 99999 | 99999 | 99999 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 200
Current | Business HVAC - DXAC | Direct Expansion HP | 65 | 107% | 99999 | 99999 | 10.7402 | 11.202 | 14.8 | 14.8 | 65 | 99999 | 99999 | 65 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 400
Current | Business HVAC - DXAC | Direct Expansion HP | 135 | 107% | 99999 | 99999 | 10.5484 | 11.002 | 14.2 | 14.2 | 65 | 99999 | 99999 | 135 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 800
Current | Business HVAC - DXAC | Direct Expansion HP | 240 | 107% | 99999 | 99999 | 9.5896 | 10.002 | 13.2 | 13.2 | 65 | 99999 | 99999 | 240 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 820
Current | Business HVAC - DXAC | Direct Expansion HP | 760 | 107% | 99999 | 99999 | 9.302 | 9.702 | 12.5 | 12.5 | 65 | 99999 | 99999 | 760 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 820
Grace | Business HVAC - DXAC | Direct Expansion AC | 64.99 | 107% | 13.814 | 14.4633 | 12.0963 | 99999 | 99999 | 99999 | 65 | 1.047 | 1.142 | 99999 | 99999 | 99999 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 200
Grace | Business HVAC - DXAC | Direct Expansion AC | 65 | 107% | 99999 | 99999 | 10.7402 | 11.202 | 14.8 | 14.8 | 65 | 99999 | 99999 | 65 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 400
Grace | Business HVAC - DXAC | Direct Expansion AC | 135 | 107% | 99999 | 99999 | 10.5484 | 11.002 | 14.2 | 14.2 | 65 | 99999 | 99999 | 135 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 800
Grace | Business HVAC - DXAC | Direct Expansion AC | 240 | 107% | 99999 | 99999 | 9.5896 | 10.002 | 13.2 | 13.2 | 65 | 99999 | 99999 | 240 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 820
Grace | Business HVAC - DXAC | Direct Expansion AC | 760 | 107% | 99999 | 99999 | 9.302 | 9.702 | 12.5 | 12.5 | 65 | 99999 | 99999 | 760 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0 | 6201.51 | 820
Grace | Business HVAC - DXAC | Direct Expansion HP | 64.99 | 107% | 13.814 | 14.4633 | 12.0963 | 99999 | 99999 | 99999 | 65 | 1.047 | 1.142 | 99999 | 99999 | 99999 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 200
Grace | Business HVAC - DXAC | Direct Expansion HP | 65 | 107% | 99999 | 99999 | 10.7402 | 11.202 | 14.8 | 14.8 | 65 | 99999 | 99999 | 65 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 400
Grace | Business HVAC - DXAC | Direct Expansion HP | 135 | 107% | 99999 | 99999 | 10.5484 | 11.002 | 14.2 | 14.2 | 65 | 99999 | 99999 | 135 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 800
Grace | Business HVAC - DXAC | Direct Expansion HP | 240 | 107% | 99999 | 99999 | 9.5896 | 10.002 | 13.2 | 13.2 | 65 | 99999 | 99999 | 240 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 820
Grace | Business HVAC - DXAC | Direct Expansion HP | 760 | 107% | 99999 | 99999 | 9.302 | 9.702 | 12.5 | 12.5 | 65 | 99999 | 99999 | 760 | 1.043 | 1 | 0.889 | 0.875 | 1 | 0.5493 | 6201.51 | 820
Back End colums no need to create Columns
| New Columns |  |  | Qualifier= | Qualifier Factor * Min Qual Efficiency
Hard input
Calculated values
| System Capacity | Minimum Qualify Efficiency | Rebate Amount
| Less than 65 MBTUH | SEER2: 14.78 | $200 per unit
| Equal to 65 MBTUH and less than 135 MBTUH | EER: 11.98 | $400 per unit
| Equal to 135 MBTUH and less than 240 MBTUH | EER: 11.77 | $800 per unit
| Equal to 20 tons and less than 63.33 tons | EER: 10.70 | $820 per summer kW reduction
| Equal to 63.33 tons and greater | EER: 10.38 | $820 per summer kW reduction
Note on M10: Lui, Chi: SEERSEER2 changed to SEER2
Note on N10: Lui, Chi: Changed from SEER2 to SEER
Note on O10: Lui, Chi: New Column Heat pump factor

## Revisions (hidden)
Date | Sheet | Cell | Change
2025-03-14 | DXAC Prog and Lookup | D6 | New back end calculated conditional efficiency values based on system capacity less than 65 Mbtuh and water cooled heat pump | More than one unit of equal capacity and efficiency?
2025-03-14 | DXAC Prog and Lookup | E6 | New back end calculated conditional efficiency values based on system capacity less than 65 Mbtuh and water cooled heat pump | If "Yes", allow input for number of units
2025-03-14 | DXAC Prog and Lookup | F6 | New back end calculated conditional efficiency values based on system capacity less than 65 Mbtuh and water cooled heat pump | If "No", Set number of units equal to "1"
2025-03-14 | DXAC Prog and Lookup | G6 | New back end calculated conditional efficiency values based on system capacity less than 65 Mbtuh and water cooled heat pump
2025-03-14 | DXAC Prog and Lookup | D17 | New factor Less Than 65 Mbtuh and water cooled heat pump
2025-03-14 | DXAC Prog and Lookup | D32 | Update conditional formula to include D6, E6,F6,G6
2025-03-14 | DXAC Prog and Lookup | D33 | Update conditional formula to include D6, E6,F6,G7
2025-03-14 | DXAC Prog and Lookup | D29 | Update value
2025-04-03 | Vlocity Matrices |  | Heat Pump Factor and revised Backend calc to include

## Test 1 (hidden)
|  |  |  | SF | Calc | SF | Calc | SF | Calc |  | Calc
Type | Capacity | Rating Type | Rating Value | SkW |  | WkW |  | kWh |  | Rebate Amount |  | From UAT | Actual
DX AC Air Cooled | 64 | SEER2 | 15.5 | 0.47 | 0.448 | 0 | 0 | 2914.71 | 2778.341 | 200
DX AC | 64 | SEER | 15.5 | -2.8 | 0.448 | 0 | 0 | -173642 | 2778.341 | 200 |  | SEER and SEER2 Water Cooled unit, | Revise note "Water cooled equipment type, select efficiency rating EER2, EER2 cannot be less than 12.94"
DX AC | 64 | EER2 | 15.5 | 0.76 | 0.448 | 0 | 0 | 4731.15 | 2778.34 | 200 |  | EER2 cannot be less than 14.78 | 12.94 | Add IEER values for Program specialist
DX AC | 65 | IEER | 16 | 0.29 | 0.293 | 0 | 0 | 1798.44 | 1815.984 | 400
DX AC | 65 | IEER2 | 16 | 0.29 | 0.293 | 0 | 0 | 1798.44 | 1815.984 | 400
DX AC | 65 | EER | 12 | 0.34 | 0.343 | 0 | 0 | 2108.51 | 2127.349 | 400
DX AC | 134 | IEER | 16 | 0.6 | 0.604 | 0 | 0 | 3720.91 | 3743.722 | 400
DX AC | 134 | IEER2 | 16 | 0.6 | 0.604 | 0 | 0 | 3720.91 | 3743.722 | 400
DX AC | 134 | EER | 12 | 0.7 | 0.707 | 0 | 0 | 4341.06 | 4385.611 | 400
DX AC | 135 | IEER | 16 | 1 | 0.951 | 0 | 0 | 6201.51 | 5896.539 | 800
DX AC | 135 | IEER2 | 16 | 1 | 0.951 | 0 | 0 | 6201.51 | 5896.539 | 800
DX AC | 135 | EER | 12 | 0.9 | 0.907 | 0 | 0 | 5581.36 | 5626.141 | 800
DX AC | 239 | IEER | 16 | 1.77 | 1.683 | 0 | 0 | 10976.67 | 10439.057 | 800
DX AC | 239 | IEER2 | 16 | 1.77 | 1.683 | 0 | 0 | 10976.67 | 10439.057 | 800
DX AC | 239 | EER | 12 | 1.59 | 1.606 | 0 | 0 | 9860.4 | 9960.354 | 800
DX AC | 240 | IEER | 14.5 | 1.42 | 1.449 | 0 | 0 | 8806.14 | 8986.941 | 1164 | 1188.31
DX AC | 240 | IEER2 | 14.5 | 1.42 | 1.449 | 0 | 0 | 8806.14 | 8986.941 | 1164 | 1188.31
DX AC | 240 | EER | 11 | 1.96 | 1.935 | 0 | 0 | 12154.96 | 12002.217 | 1607 | 1587
DX AC | 759 | IEER | 14.5 | 4.5 | 4.583 | 0 | 0 | 27906.8 | 28421.2 | 3690 | 3758.02
DX AC | 759 | IEER2 | 14.5 | 4.5 | 4.583 | 0 | 0 | 27906.8 | 28421.2 | 3690 | 3758.02
DX AC | 759 | EER | 11 | 6.19 | 6.121 | 0 | 0 | 38387.35 | 37957.01 | 5076 | 5018.01
DX AC | 760 | IEER | 14 | 5.63 | 5.971 | 0 | 0 | 34914.5 | 35914.185 | 4617 | 4748.78
DX AC | 760 | IEER2 | 14 | 5.63 | 5.971 | 0 | 0 | 34914.5 | 35914.185 | 4617 | 4748.78
DX AC | 760 | EER | 10.4 | 5.07 | 4.674 | 0 | 0 | 31441.66 | 28985.021 | 4157 | 3832.57
Type | Capacity | Rating Type | Rating Value | SkW |  | WkW |  | kWh |  | Rebate Amount |  | From UAT | Actual
DX AC Water Cooled | 64 | SEER2 | 13 | -0.21 |  | 0 |  | -1139.53 |  | 200 |  | SEER2 cannot be less than 12.94 | SEER2: 14.78, Negative values due to rating values not correct, used 14.94, Revise note "Water cooled equipment type, select efficiency rating EER2, EER2 cannot be less than 12.94" Can we limit efficiency rating type to EER2 fo water cooled system less than 65 mbtuh?
DX WC | 64 | SEER | 15 | -3.11 |  | 0 |  | -16875.86 |  | 200 |  | SEER and SEER2 cannot be less than 12.94 | SEER: 15.47
DX WC | 64 | EER2 | 13 | 0.04 |  | 0 |  | 217.05 |  | 200 |  | kWh seems low | Revise note "Water cooled equipment type, select efficiency rating EER2, EER2 cannot be less than 12.94" Can we limit efficiency rating type to EER2 fo water cooled system less than 65 mbtuh?
DX WC | 65 | IEER | 16 | 0.25 |  | 0 |  | 1356.58 |  | 400
DX WC | 65 | IEER2 | 16 | 0.25 |  | 0 |  | 1356.58 |  | 400
DX WC | 65 | EER | 12 | 0.3 |  | 0 |  | 1627.9 |  | 400
DX WC | 134 | IEER | 16 | 0.52 |  | 0 |  | 2821.69 |  | 400
DX WC | 134 | IEER2 | 16 | 0.52 |  | 0 |  | 2821.69 |  | 400
DX WC | 134 | EER | 12 | 0.61 |  | 0 |  | 3310.06 |  | 400
DX WC | 135 | IEER | 16 | 0.88 |  | 0 |  | 4775.16 |  | 800
DX WC | 135 | IEER2 | 16 | 0.88 |  | 0 |  | 4775.16 |  | 800
DX WC | 135 | EER | 12 | 0.79 |  | 0 |  | 4286.79 |  | 800
DX WC | 239 | IEER | 16 | 1.55 |  | 0 |  | 8410.8 |  | 800
DX WC | 239 | IEER2 | 16 | 1.55 |  | 0 |  | 8410.8 |  | 800
DX WC | 239 | EER | 12 | 1.39 |  | 0 |  | 7542.59 |  | 800
DX WC | 240 | IEER | 14.5 | 1.24 |  | 0 |  | 6728.64 |  | 1017
DX WC | 240 | IEER2 | 14.5 | 1.24 |  | 0 |  | 6728.64 |  | 1017
DX WC | 240 | EER | 11 | 1.71 |  | 0 |  | 9279.01 |  | 1402
DX WC | 759 | IEER | 14.5 | 3.94 |  | 0 |  | 21379.71 |  | 3231
DX WC | 759 | IEER2 | 14.5 | 3.94 |  | 0 |  | 21379.71 |  | 3231
DX WC | 759 | EER | 11 | 5.41 |  | 0 |  | 29356.4 |  | 4436
DX WC | 760 | IEER | 14 | 4.93 |  | 0 |  | 26751.76 |  | 4043
DX WC | 760 | IEER2 | 14 | 4.93 |  | 0 |  | 26751.76 |  | 4043
DX WC | 760 | EER | 10.4 | 4.43 |  | 0 |  | 24038.6 |  | 3633
Type | Capacity | Rating Type | Rating Value | SkW | Calc | WkW | Calc | kWh | Calc | Rebate Amount
DX HP Water Cooled | 64 | SEER2 | 13 | -0.21 |  | 0 |  | -1139.53 |  | 200
DX WC HP | 64 | SEER | 15 | -3.11 |  | 0 |  | -16875.86 |  | 200
DX WC HP | 64 | EER2 | 13 | 0.04 |  | 0.02 |  | 217.05 |  | 200
DX WC HP | 65 | IEER | 16 | 0.25 |  | 0.12 |  | 1356.58 |  | 400
DX WC HP | 65 | IEER2 | 16 | 0.25 |  | 0.12 |  | 1356.58 |  | 400
DX WC HP | 65 | EER | 12 | 0.3 | 0.292 | 0.14 | 0.136 | 1627.9 | 1540.628 | 400 | 400
DX WC HP | 134 | IEER | 16 | 0.52 |  | 0.25 |  | 2821.69 |  | 400
DX WC HP | 134 | IEER2 | 16 | 0.52 |  |  |  | 2821.69 |  | 400
DX WC HP | 134 | EER | 12 | 0.61 | 0.602 | 0.29 | 0.281 | 3310.06 | 3176.064 | 400 | 400
DX WC HP | 135 | IEER | 16 | 0.88 |  | 0.42 |  | 4775.16 |  | 800
DX WC HP | 135 | IEER2 | 16 | 0.88 |  |  |  | 4775.16 |  | 800
DX WC HP | 135 | EER | 12 | 0.79 | 0.772 | 0.38 | 0.361 | 4286.79 | 4074.457 | 800 | 800
DX WC HP | 239 | IEER | 16 | 1.55 |  | 0.74 |  | 8410.8 |  | 800
DX WC HP | 239 | IEER2 | 16 | 1.55 |  |  |  | 8410.8 |  | 800
DX WC HP | 239 | EER | 12 | 1.39 | 1.367 | 0.67 | 0.689 | 7542.59 | 7213.298 | 800 | 800
DX WC HP | 240 | IEER | 14.5 | 1.24 |  |  |  | 6728.64 |  | 1017
DX WC HP | 240 | IEER2 | 14.5 | 1.24 |  |  |  | 6728.64 |  | 1017
DX WC HP | 240 | EER | 11 | 1.71 | 1.647 | 0.82 | 0.77 | 9279.01 | 8692.017 | 1402 | 1350.54
DX WC HP | 759 | IEER | 14.5 | 3.94 |  |  |  | 21379.71 |  | 3231
DX WC HP | 759 | IEER2 | 14.5 | 3.94 |  |  |  | 21379.71 |  | 3231
DX WC HP | 759 | EER | 11 | 5.41 | 5.209 | 2.6 | 2.435 | 29356.4 | 27488.504 | 4436 | 4271.08
DX WC HP | 760 | IEER | 14 | 4.93 |  |  |  | 26751.76 |  | 4043
DX WC HP | 760 | IEER2 | 14 | 4.93 |  |  |  | 26751.76 |  | 4043
DX WC HP | 760 | EER | 10.4 | 4.43 | 3.977 | 2.13 | 1.859 | 24038.6 | 20990.981 | 3633 | 3261.52

## Test 2 04112025 (hidden)
|  |  |  | UAT | Calculator | UAT | Calculator | UAT | Calculator | UAT | Calculator
Type | Capacity | Rating Type | Rating Value | SkW |  | WkW |  | kWh |  | Rebate Amount |  | From UAT comments | DX Calculator commets
DX AC Air Cooled | 64 | SEER2 | 15.5
DX AC | 64 | SEER | 15.5
DX AC | 64 | EER2 | 15.5
DX AC | 65 | IEER | 16
DX AC | 65 | IEER2 | 16
DX AC | 65 | EER | 12
DX AC | 134 | IEER | 16
DX AC | 134 | IEER2 | 16
DX AC | 134 | EER | 12
DX AC | 135 | IEER | 16
DX AC | 135 | IEER2 | 16
DX AC | 135 | EER | 12
DX AC | 239 | IEER | 16
DX AC | 239 | IEER2 | 16
DX AC | 239 | EER | 12
DX AC | 240 | IEER | 14.5
DX AC | 240 | IEER2 | 14.5
DX AC | 240 | EER | 11
DX AC | 759 | IEER | 14.5
DX AC | 759 | IEER2 | 14.5
DX AC | 759 | EER | 11
DX AC | 760 | IEER | 14
DX AC | 760 | IEER2 | 14
DX AC | 760 | EER | 10.4
|  |  |  | UAT | Calculator | UAT | Calculator | UAT | Calculator | UAT | Calculator
Type | Capacity | Rating Type | Rating Value | SkW |  | WkW |  | kWh |  | Rebate Amount |  | From UAT comments | DX Calculator commets
DX AC Water Cooled | 64 | SEER2 | 13
DX WC | 64 | SEER | 15
DX WC | 64 | EER2 | 13
DX WC | 65 | IEER | 16
DX WC | 65 | IEER2 | 16
DX WC | 65 | EER | 12
DX WC | 134 | IEER | 16
DX WC | 134 | IEER2 | 16
DX WC | 134 | EER | 12
DX WC | 135 | IEER | 16
DX WC | 135 | IEER2 | 16
DX WC | 135 | EER | 12
DX WC | 239 | IEER | 16
DX WC | 239 | IEER2 | 16
DX WC | 239 | EER | 12
DX WC | 240 | IEER | 14.5
DX WC | 240 | IEER2 | 14.5
DX WC | 240 | EER | 11
DX WC | 759 | IEER | 14.5
DX WC | 759 | IEER2 | 14.5
DX WC | 759 | EER | 11
DX WC | 760 | IEER | 14
DX WC | 760 | IEER2 | 14
DX WC | 760 | EER | 10.4
|  |  |  | UAT | Calculator | UAT | Calculator | UAT | Calculator | UAT | Calculator
Type | Capacity | Rating Type | Rating Value | SkW | Calc | WkW | Calc | kWh | Calc | Rebate Amount |  | From UAT comments | DX Calculator commets
DX HP Water Cooled | 64 | SEER2 | 13
DX WC HP | 64 | SEER | 15
DX WC HP | 64 | EER2 | 13
DX WC HP | 65 | IEER | 16
DX WC HP | 65 | IEER2 | 16
DX WC HP | 65 | EER | 12
DX WC HP | 134 | IEER | 16
DX WC HP | 134 | IEER2 | 16
DX WC HP | 134 | EER | 12
DX WC HP | 135 | IEER | 16
DX WC HP | 135 | IEER2 | 16
DX WC HP | 135 | EER | 12
DX WC HP | 239 | IEER | 16
DX WC HP | 239 | IEER2 | 16
DX WC HP | 239 | EER | 12
DX WC HP | 240 | IEER | 14.5
DX WC HP | 240 | IEER2 | 14.5
DX WC HP | 240 | EER | 11
DX WC HP | 759 | IEER | 14.5
DX WC HP | 759 | IEER2 | 14.5
DX WC HP | 759 | EER | 11
DX WC HP | 760 | IEER | 14
DX WC HP | 760 | IEER2 | 14
DX WC HP | 760 | EER | 10.4